ORICK COMMUNITY SERVICES DISTRICT   CROSS-CONNECTION CONTROL (CCC) PLAN

To comply with section 3.1.4 of the Cross-Connection Control Policy Handbook (CCCPH),  each public water system (PWS) must submit a written Cross-Connection Control (CCC) Plan to the State Water Board for review. This template is provided as a resource for community water systems with 200 or fewer service connections. A PWS may choose to use this template or create its own plan. Please note that completing and submitting this form to the State Water Board does not guarantee that the State Water Board will approve the submitted plan.

Instructions: Complete every blank in this template including answering all yes or no questions and attaching documents. Refer to the Cross-Connection Control Policy

Handbook for definitions and detailed explanations of all CCC program requirements.

Public Water System Information

| Public Water System Name: | Orick Community Services District |
| --- | --- |
| Public Water System Number: | CA1200701 |
| Number of single-family residential service connections: | 113 |
| Number of multifamily residential service connections (duplex, apartments, etc.): | 5 |
| Number of commercial service connections: | 25 |
| Number of industrial service connections: | 0 |
| Number of agricultural irrigation service connections: | 0 |
| Number of landscape irrigation service connections: | 0 |
| Water System Ownership Type (check one): XPublic ☐State or Federal Government ☐CPUC regulated ☐Mutual Water Co. ☐ HOA ☐Private – Other ☐Other, describe: |  |
| Add any additional details: |  |

CCC Legal Authority

All PWSs are required to have the legal authority to implement a CCC program.

| Legal Authority Type: | X Operating rules ☐ Ordinance Board Adoption ☐ Bylaw ☐ Other – describe: |
| --- | --- |
| Date legal authority adopted by PWSs governing body (Board, City, County, etc.): | 07/31/2025 |

Orick Community Services District Cross-Connection Control Plan July 31st, 2025

| Attach a copy of the document which provides CCC enforcement authority (ordinance, bylaws, operating rules, etc). |  |
| --- | --- |
| At what location(s) is backflow protection required? | X At the meter / service connection only ☐ Internal ☐Both |
| List the corrective actions the PWS will implement in the event a water user fails to comply with the provisions of the PWSs cross-connection control program. | X Noticing letter X Threaten to shutoff letter ☐ Fines X Shut off water X Other – describe below. |
| Describe other corrective action methods: For non compliance, Orick CSD will remove the meter from the premises until Orick CSD is satisfied a new BPA has been installed or repaired and re-tested by a certified BPA Tester. |  |

Cross-Connection Control Coordinator Contact Information

| Name: | Trevor H Avram |
| --- | --- |
| Phone number: | W. (707)488-5741 M. (530)520-2744 |
| Email: | orickcsd@gmail.com, avramtrevor@gmail.com |
| Address: | 101 Swan Rd Orick CA, 95555 |
| Coordinator qualifications (experience, training, and/or certifications): | Operator D1 Operator# 53230 |

Hazard Assessments

The cross-connection control specialist who will review and/or conduct our initial hazard assessments is certified by __Brian McNeill__ (AWWA certified/DDW recognized organization) and certification number 10383 Expiration Date 6/30/2028 Note: certified cross-connection control specialist must meet the requirements of CCCPH ---

Describe your hazard assessment procedures: X In person site survey ☐ Questionnaire completed by customer ☐ Phone/email ☐Use of mapping software X File Review ☐ Plan Check ☐Other methods:

Describe the certified cross-connection control specialist’s role: To assess any cross connection control hazards and provide the operator with his recommendations to remediate the hazard.

We will conduct initial hazard assessments of the user premises within its service area no later than: Hazard assessments completed prior to the adoption of the CCCPH will be considered as an initial hazard assessment provided that such hazard assessments and associated backflow protection provide protection consistent with the CCCPH 3.2.1;

Orick Community Services District Control Plan July 31st, 2025

Pursuant to CCCPH 3.2.1 (e). A new hazard assessment must be performed if; (1) if a user premises changes account holder, excluding single-family residences; (2) if a user premises is newly or re-connected to the PWS; (3) if evidence exists of changes in the activities or materials user’s premises; (4) if backflow from a user’s premises occurs; (5) periodically, as identified in the PWS’s Cross-Connection Control Plan required pursuant to CCCPH section 3.1.4.; (6) if the State Water Board requests a hazard assessment of a user’s premises; or (7) if the PWS concludes an existing hazard assessment may no longer accurately represent the degree of hazard. The (new) property owner / account holder at their expense must have a new assessment performed if any of the above conditions are met. Orick CSD will use the recommendations from the specialist to enforce our CCCP.

We will conduct ongoing hazard assessments of each service connection on our list pursuant to CCCPH section 3.2.1.;

We will incorporate the recommendations of any hazard assessment no later than 30 days after the new hazard assessment is complete.

Describe additional details about your PWSs hazard assessment procedure:

Is auxiliary water used in our service area? X No

(Attach a copy of an existing completed hazard assessment report for evaluation)

Backflow Preventer Inventory and Testing Procedures

| Does your PWS have backflow prevention assemblies installed? | X YES – How many? 12 |
| --- | --- |
| If “yes”, attach a listing of your current inventory. See example list in Attachment 1. |  |
| Does your PWS have any backflow prevention assemblies that are buried (or below grade)? | X YES |
| Does your service area experience freezing conditions during the winter? | X NO |
| Does your PWS have non-testable backflow preventers at PWS facilities? | X NO |
| If “yes”, attach a listing of your current inventory. See example list in Attachment 2. |  |
| Required backflow prevention assembly maintenance, repair, or replacement will happen within ___30______ days after identification. |  |
| If the same testers are used regularly, provide the name(s) and certification(s) of the testers used at the PWS: Brian McNeill - Certification # AWWA - 10383 |  |
| I certify that all individuals who test backflow prevention assemblies are certified by an ANSI accredited or DDW recognized organization. | X YES ☐ Not Applicable |
| I certify that our testers’ field test kit is accurate and recently verified. | X YES ☐ Not Applicable |
| I certify that testers provide the PWS with copies of the backflow prevention assembly test results. | X YES ☐ Not Applicable |

| What notification methods do you use to inform customers that their BPA test is due? | X Letter ☐ Phone ☐ Email ☐ Other – describe: |
| --- | --- |
| Describe your PWSs procedure for ensuring all backflow prevention assemblies and air gap installations are Tested at least annually: Yes | Orick CSD’s policy is to have all the backflow devices on our CCCP list tested annually in September/October. The customer is notified and the testing is billed to their account. |
| What penalties exist for unresponsive customers that do not test BPAs? | ☐ Fines Fine amounts are: $ _____ to _____ X Water shutoffs ☐ Other – describe: |
| What penalties exist (Ordinances or Rules of Service) for failed, tampered, and missing BPAs? | ☐ Fines Fine amounts are: $ _____ to X Water shutoffs ☐ Other – describe: |

Backflow Incident Response, Notification, and Reporting

In the event of a suspected or known backflow incident, I certify that our PWS system will:

| Respond and investigate all suspected backflow incidents by responding to and documenting complaints, conducting water quality sampling, and checking pressure. | X YES |
| --- | --- |
| Notify regulatory agency within 24 hours of discovering a known or suspected backflow event | X YES |
| Regulatory Authority Contact Information: SWRCB Division of Drinking Water, Klamath District 01, Redding Office General Office: (530)224-4800 General Email: dwpredding@waterboards.ca.gov |  |
| If directed by the regulatory agency, notify customers with appropriate public notification within 24 hours. | X YES |
| Complete a Backflow Incident Report at the request of the regulatory agency. | X YES |
| Include the name(s) of personnel who respond to water quality complaints and suspected backflow incidents: Trevor H Avram / Bill Allen |  |

Orick Community Services District Cross-Connection Control Plan July 31st, 2025

Public Outreach and entity coordination

What method(s) are used to educate your customers, staff, and community about backflow protection and cross-connection control: (select all that apply) ☐ Periodic water bill inserts ☐Pamphlet distribution ☐ New customer documentation ☐ Customer Emails X Consumer Confidence Reports ☐Public Events X Website ☐Other:

Include additional details about public outreach:

Describe coordination with the local entities about your PWSs CCC program. Orick Volunteer Fire Department (OVFD) Redwood National Park (RNP) Yurok Tribe (YEDC)

Orick Community Services District Cross-Connection Control Plan July 31st, 2025

Record Keeping

CCC program documents, including backflow prevention assembly test reports, hazard assessments, contracts, and our inventory of all backflow preventers are stored using the following method(s): DIGITAL/HARD COPY BOTH

Our PWS stores all records in accordance with section 3.5.1 of the CCCPH, which includes public outreach materials, and backflow prevention assembly testing, repair, inspection, and maintenance records for at least three years. YES

Describe any additional details:

Orick Community Services District Cross-Connection Control Plan July 31st, 2025

Certification

I certify that the information submitted in this Cross-Connection Control Plan is accurate and we will comply with the Cross-Connection Control Policy Handbook July 31st, 2025

Our public water system will ensure its Cross-Connection Control Plan is at all times representative of the current operation of its Cross-Connection Control Program.

Attached are copies of our hazard assessment, backflow prevention assembly and  backflow preventer inventories, and our Cross-Connection Control enforcement authority.

Name: Trevor H Avram                          Role: Operator

Signature:                                               Date:

DDW / LPA Review:

The public water system has demonstrated compliance with the Cross-Connection Control

Plan requirements of the CCCPH.

Name:                                                Title:

Signature:                                           Date:

Orick Community Services District Cross-Connection Control Plan July 31st, 2025

ATTACHMENT 1: BACKFLOW PREVENTION ASSEMBLY INVENTORY AND HAZARD ASSESSMENT

| Inventory of Backflow Prevention Assemblies |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Location (clearly describe address and specific location) | Assembly Type (RP, DCV, AG, PVB, etc.) | Assembly Size | Manufacturer name, model, and Serial Number | Installation: (horizontal, vertical, above/below grade) | Identified Potential Onsite Hazard |
| 159 Hufford Rd | DCV | 3/4” | Wilkins 850, Serial #2090 | Horizontal | Private Well |
| 121140 Hwy 101 Orick Theater | DCV | 3/4” | Wilkins 975 XL Serial # A190278 | Horizontal | Private Well |
| 121130 Hwy 101 Roosevelt Base | DCV | 1” | Watts LF007M1QT Serial # 008390 | Horizontal | Private Well |
| Foothill Dr. Behind Tank 1 | DCV | 1” | Watts LF007M1QT Serial #152851 | Horizontal | Private Well |
| 119933 Hwy 101 (Blue Barn) | DCV | 1” | Wilkins 850 XL Serial # AJG7705 | Horizontal | Private well |
| 121175 Hwy 101 (Orick Market) | DCV | 3/4” | Watts 007M1GT Serial # 09434 | Horizontal | Private well |
| 120666 Hwy 101 (White Barn) | DCV | 3/4” | Wilkins 850 Serial # A113414 | Horizontal | Private well |
| 120120 Hwy 101 | DCV | 1” | Wilkins 350 XL Serial # Unreadable | Horizontal | Private spring |
| 400 Old State Hwy | DCV | 1” | Wilkins 350 XL Serial # A222343 | Horizontal | Private booster pump |
| 119441 Hwy 101 Thomas Kuechel Visitors Center | No Device (A new device needs to be installed) |  |  |  | Fire Suppression |
| 121200 Hwy 101 South Operation Center | DCV |  | FEBCO 850 Serial # F020 703 1000 | Horizontal | Fire Suppression |
| 121200 Hwy 101 South Operation Center | SCV Single Check (Needs to be Replaced within 10 years) |  |  | Horizontal | Fire Suppression |

RP: Reduced pressure principle backflow prevention assembly

DCV: Double check valve backflow prevention assembly

AG: Air Gap

PVB: Pressure Vacuum Breaker backflow prevention assembly

Orick Community Services District Cross-Connection Control Plan July 31, 2025